Mechanical Ventilation with Heat Recovery (MVHR)

A Mechanical Ventilation System with Heat Recovery (MVHR) shall be installed in accordance with the manufacturer’s instructions. A comprehensive system design incorporating design commissioning data shall be supplied to the installer by the manufacturer detailing the layout and all system components. The installer shall follow the design using the recommended components and shall provide completed installed performance test documentation. All designs and installations shall meet with the requirements of Building Regulations and Best Practice guidance such Domestic Ventilation Compliance Guide 2010 and the NHBC Standard Chapter 3.2.

To be terminated externally using the Titon Q Plus High Flow Brick to ensure performance is not compromised.

To be terminated externally via a Titon roof terminal that meets both the system and roof design and intended for use with continuous mechanical ventilation systems having a maximum airflow resistance of 3Pa.

All switches to be provided by Titon and shall be engraved to show the switch designation such as Boost, SUMMERboost® or Summer Mode and as appropriate to the required operation. Switches should be located in accordance with client instruction and wired in accordance with the chosen unit product handbook and current IET wiring requirements.

Titon HRV1.6 Q Plus HMB Eco – Consultant Specification

The MVHR unit shall be the Titon HRV1.6 Q Plus HMB Eco wall mounted with integral automatic 100% Summer Bypass and incorporating an automatic SUMMERboost® to accelerate the airflow to the maximum rate when the Summer Bypass is engaged. The unit shall also incorporate zero volt boost switching, an adjustable boost Timer Overrun and Humidity boost facility and all features shall be activated/deactivated as required in accordance with client instructions at commissioning stage. Automatic Frost Protection must be by means of polynomial speed reduction of the supply fan speed to prolong fresh air supply. The HRV shall be made using light weight EPP giving high levels of thermal insulation surrounded by a sturdy metal enclosure finished in a white powder coat paint measuring 600mm wide x 505mm high (excluding ports) x 353mm deep (363mm with mounting bracket) weighing 22kg max.  The MVHR unit shall be SAP Q qualified and capable of a SFP of 0.49 w/l/s and a Heat Exchanger efficiency of 89%.The MVHR Unit shall also have an EU compliant energy rating label with a minimum rating of A and be CE certified and manufactured under BS EN ISO 9001 and BS EN ISO 14001 and have a 3 year parts & labour guarantee.

Eco HMB version options

MVHR Units to be wired to a Titon auralite® low voltage indicator display located conveniently to allow occupant to easily see a visible indication of the MVHR unit status including normal running, Summer Bypass, boost and frost protection modes and include a filter change indicator, system fault and (prolonged) boost alerts.

Unit to be terminated externally using the Titon Q Plus High Flow Brick to ensure performance is not compromised.